SECTION 11-14-00

PEDESTRIAN CONTROL EQUIPMENT

- GENERAL

SECTION INCLUDES

Security Full Height Turnstiles of the following type:

Inclusion of rotor assembly, shield assembly, barrier assembly, mechanism housing and ceiling plate. (Turnlock 100)

RELATED SECTIONS

Section 09600- Flooring

Section 16123- Electrical Supply Termination

Section 11 14- Pedestrian Control Equipment

Section 11 14 13.19- Turnstiles

Section 11 14.53- Pedestrian Security Equipment

Section 08400- Entrances and Storefront

REFERENCES

American National Standards Institute (ANSI):

ANSI Z97.1 - Safety Glazing Material Used in Buildings.

Fenestration & Glazing Industry Association (FGIA)- previously known as the American Architectural Manufacturers Association (AAMA):

AAMA 2604- Voluntary specification, Performance requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusion and Panels.

AAMA 2605- Voluntary specification, performance requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

American Society for Testing and Materials (ASTM):

ASTM A 36- Standard Specification for Carbon Structural Steel

ASTM A 276- Standard Specification for Stainless Steel Bars and Shapes

ASTM A 480/A 480M- Standard Specification for General Requirements for Flat Rolled Stainless and Heat-Resisting Steel Plate, Sheet and Strip

ASTM A 666- Standard Specification for Annealed or Cold-Worked Austenitic Stainless-Steel Sheet, Strip, Plate and Flat Bar.

ASTM B 209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

ASTM B 221- Standard Specification for Aluminum and Aluminum- Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

Underwriters Laboratories Inc. (UL)

UL Standard 294

SUBMITTALS

Submit under provisions of Section 01 30 00 - Administrative Requirements.

Product Data: Submit manufacturer's product data sheets, including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions and finishes:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods.

Shop Drawings: Submit manufacturer's shop drawings, including pertinent dimensions, general construction, component connections and locations, anchorage methods and locations, safety plus sensors, hardware and installation details.

Operation and Maintenance Manual: Submit manufacturer's operation and maintenance manual.

QUALITY ASSURANCE

Manufacturer's Qualifications:

Specialization in the supply of security optical turnstiles with a minimum of 10 years’ experience.

Factory-Trained supervisor shall be supplied during installation of the full-height security turnstile.

Installer's Qualifications:

Local factory-trained field service technician shall be provided to competently service the security turnstile; and to provide for the local support of the customer’s service technicians in the event the customer’s trained technician is not available. In the event there are no service technicians matching the aforementioned description and requirements, the manufacturer, Boon Edam, Inc., is to be utilized for service.

Local certified Boon Edam, Inc. distributor required if not being installed by the manufacturer, Boon Edam, Inc.

Approved by manufacturer.

Single Source Requirements: To the greatest extent possible provide products specified in this section from a single manufacturer.

DELIVERY, STORAGE, AND HANDLING

Delivery: Deliver materials to site protected from damage.

Storage: Store materials in clean, dry area indoors, off-ground in manufacturer's unopened packaging until ready for installation and in accordance with manufacturer's instructions.

Handling: Protect materials and finish from damage during handling and installation.

Approximate Weight of Crate: 800 lbs. (2 x 800 lbs. for Tandem Unit).

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.

The Turnlock 100 Full-Height Security Turnstile installs on finished floor only.

MAINTENANCE SERVICE

The manufacturer shall offer a dispatch procedure that shall be available 24 hours per day, 365 days per year to facilitate proper service capability.

A manufacturer's designated service contact shall obtain malfunction information and dispatch appropriate service provider to project location.

Submission for maintenance service via Boon Edam, Inc. Phone: 910-984-8094 or us.techsupport@boonedam.com

A geographically assigned installation provider shall be trained and certified to provide maintenance service.

COORDINATION AND SCHEDULING

Conference: Convene a pre-installation conference to establish procedures to maintain optimum working conditions and to coordinate this work with related and adjacent work per Owner request.

Coordinate sizes and locations of recesses in concrete if applicable.

Field Measurements: Verify actual dimensions of openings to receive security turnstiles by field measurements before fabrication and indicate on shop drawings.

WARRANTY

Warranty: Provide manufacturer's standard warranty against defects in materials and workmanship. Warranty shall be one year from the date of installation.

Warranty Period: 1 Year (12 Months):

During the warranty period a factory-trained technician shall perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair and a completed inspection form shall be submitted to the Owner.

The Warranty excludes glass breakage, normal wear on finishes or damage that occurs due to abuse, misuse or acts of God.

- PRODUCTS

MANUFACTURERS

Acceptable Manufacturer: Boon Edam, Inc. 402 McKinney Parkway, Lillington NC 27546. (910) 814-3800 Fax: (910) 814-3889 Website: www.boonedam.us

Substitutions: Not permitted.

Requests for substitutions will be considered in accordance with the provisions of Section 01 60 00 - Product Requirements.

SECURITY FULL-HEIGHT TURNSTILE

Security Full-Height Turnstile Construction:

Provide Mechanism Housing constructed from structural steel channel. All electrical and mechanical components to be attached to the channel. The channel is to be covered by a 16-gauge stainless steel cover.

Install 5” (126.9 mm) 17-4 PH Stainless Steel High Impact Channel Studs designed to provide enhanced stability and support.

Provide Ceiling Plate fabricated from 16-gauge steel or stainless steel attached to the mechanism housing and spans the shield assembly, providing for stability and support.

Provide Rotor Assembly consisting of 3 rotor posts set to a position of 120 degrees apart from each other. The top and bottom of the rotor assembly to be held together by a flange. Rotor posts are also to be attached to the flange.

Barrier posts to consist of eleven arms equally spaced at an offset to the rotor assembly. The barrier post to be constructed from 2” x 4 11” gauge carbon steel tubing with carbon steel 1 ½” schedule 40 pipe barrier arms (galvanized and powder coated units) (1 ¼” schedule pipe for all stainless-steel units)

Shield assembly to consist of 2 welded frames that are installed adjacent to each other to form the passageway. The shield assembly to be constructed from 2” x 2” square tubes and 1 3/8” round tubes (galvanized and powder coated OR stainless steel for stainless steel units.)

Arms to be 1 ¼” schedule 40 steel pipe, each arm (galvanized and powder coated) has plastic caps on the end; 1 ¼” schedule 40 #304 stainless steel pipe with rounded, spun closed and polished ends (for all stainless-steel units)

Bottom Bearing to be pre-greased thrust Axial Deep Groove Ball Bearing. The bearing to be installed on a 9” x 1” clear anodized aluminum base plate. Base plate to attach to the floor with 3 anchor bolts 3/8” x 4” long. Dynamic load capacity in excess of 14,300 lbs., a static load capacity of over 39,500 lbs. and maximum rated RPM of 1800.

Security Full-Height Turnstile Equipment:

Provide a one-way mechanical turnstile using a steel rachet assembly to direct traffic flow.

Electric controls to be available in both entrance and exit directions. Controls may be fail- lock/secure (FL) and fail-safe (FS) or any combination, in either controlled direction.

All turnstiles to be built to the customer’s specified configuration. Configuration to be easily reconfigured in the field without any additional parts.

Electric turnstiles to use a heavy-duty electro-mechanical ratchet and pawl operating mechanism to restrict traffic flow. All electrical controls to be low voltage 24 VDC. (Step-down transformer is supplied as a standard item- selectable to either 110 VAC or 220 VAC input voltage).

Standard self-centering feature to automatically return rotor assembly to the home position assuring the correct starting position of the rotor.

Operating mechanism to be fabricated using extra heavy-duty components to accommodate the high rotor weight. Rotation speed to be controlled by hydraulic shock absorber gear system. All internal operating components are enclosed in fabricated stainless steel top cover.

Concealed top and bottom bearings are to be provided for free easy rotation in hostile environments.

Performance/ Throughput Requirements:

General: Provide security full-height turnstiles that have been designed to provide passage of traffic in one direction only. Throughput is defined as the number of people per minute which can pass through an optical turnstile in one direction only. Average throughput shall be approximately 15-20 people per minute. Tandem units’ throughput to be 2 units at 15-20 people per minute.

Finish:

Hot dipped galvanized (Powder Coat and #304 Stainless Steel available upon request)

Security Full Height Enhanced Components

- Turnlock Security 100- Full Height Turnstile to be installed with BE-Secure Overhead Detection System (Factory Special Request, Only Available with top channel installation).

        - Provide system with anti-piggybacking sensor utilizing Time-of-Flight (TOF) measurement principles, combined with artificial intelligence (AI) algorithms. System to determine distance information with 500 pixels of resolution.

        - Four states of passage must be distinguished which include: Detection Area Free, one person passed through detection area, and more than one person is within the detection area and person has entered and backed out of detection area.

        - Finish to be Black Powder Coat or #4 Brushed Stainless Steel

Additional Required Components:

Turnlock Security 100 Full-Height Turnstile to be installed with the following additional options as specified.

Remote release pushbutton

Solenoid Activation Switch

Out of use lock

Credential Reader mounting weather-resistant box

Heel protectors

- EXECUTION

PREPARATION

Installer must examine the location and advise the Contractor of any site conditions unacceptable for proper installation of product. The minimum conditions necessary to initiate installation are:

Floor must be dead level at any point within the footprint of the turnstile.

Finished floor must be installed.

Floor must be complete with conduit supplied to meet manufacturer’s specified drawings.

Power supply (110-240VAC) and communication must be installed.

INSTALLATION

    - Install turnstile in accordance with manufacturer’s printed instructions. Set unis level, plumb, and with uniform hairline joints. Anchor securely in place. Use only factory trained installers.

FIELD QUALITY CONTROL

Manufacturer's Field Services:

Manufacturer's representative shall provide technical assistance and guidance for installation of Turnlock 100 Full-Height Security Turnstile.

ADJUSTING

    - Installer shall adjust turnstile for smooth operation and proper performance.

DEMONSTRATION AND TRAINING

    - A factory-trained installer shall demonstrate to the Owner’s maintenance crew the proper operation of the Turnlock 100 Full-Height Security Turnstile and the necessary service requirements such as lubrication, cleaning and inspection of components upon completion of installation.

CLEANING AND PROTECTION

    - Clean metal surfaces carefully using manufacturer’s suggested cleaning materials.

END OF SECTION