SECTION 11-14-00

PEDESTRIAN CONTROL EQUIPMENT

- GENERAL

SECTION INCLUDES

One-way handicapped full height security gate of the following type:

Provide complete system that has been fabricated and tested for proper operation at the factory. Including gate frame, door wings, hardware, hydraulic closer unit as required for installation. (Turnlock Side Gate Electric One-Way Handicapped Gate)

RELATED SECTIONS

Section 09600- Flooring

Section 16123- Electrical Supply Termination

Section 11 14- Pedestrian Control Equipment

REFERENCES

American National Standards Institute (ANSI):

ANSI Z97.1 - Safety Glazing Material Used in Buildings.

ANSI 117.1 – Accessible and Usable Buildings and Facilities

Fenestration & Glazing Industry Association (FGIA)- previously known as the American Architectural Manufacturers Association (AAMA):

AAMA 2604- Voluntary specification, Performance requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusion and Panels.

AAMA 2605- Voluntary specification, performance requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

American Society for Testing and Materials (ASTM):

ASTM B 221- Standard Specification for Aluminum and Aluminum- Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

Underwriters Laboratories Inc. (UL).

UL Standard 325

UL Standard 2593

SUBMITTALS

Submit under provisions of Section 01 30 00 - Administrative Requirements.

Product Data: Submit manufacturer's product data sheets, including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions, and finishes:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods.

Shop Drawings: Submit manufacturer's shop drawings, including pertinent dimensions, general construction, component connections and locations, anchorage methods and locations, hardware, and installation details.

Operation and Maintenance Manual: Submit manufacturer's operation and maintenance manual.

QUALITY ASSURANCE

Manufacturer's Qualifications:

Specialization in the supply of full-height side gates with a minimum of 10 years’ experience.

Factory-Trained supervisor shall be supplied during installation of full-height side gates.

Installer's Qualifications:

Locally located factory-trained field service technicians shall be provided to competently service the security turnstile; and to provide for the local support of the customer’s service technicians in the event the customer’s trained technician is not available. In the event there are no service technicians matching the aforementioned description and requirements, the manufacturer, Boon Edam, Inc., is to be utilized for service.

Local certified Boon Edam, Inc. distributor required if not being installed by the manufacturer, Boon Edam, Inc.

Approved by manufacturer.

Single Source Requirements: To the greatest extent possible provide products specified in this section from a single manufacturer.

DELIVERY, STORAGE, AND HANDLING

Delivery: Deliver materials to site protected from damage.

Storage: Store materials in clean, dry area indoors, off ground in manufacturer's unopened packaging until ready for installation and in accordance with manufacturer's instructions.

Handling: Protect materials and finish from damage during handling and installation.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.

The Turnlock Side Gate installs on finished floor only.

MAINTENANCE SERVICE

The manufacturer shall offer a dispatch procedure that shall be available 24 hours per day, 365 days per year to facilitate proper service capability.

A manufacturer's designated service contact shall obtain malfunction information and dispatch appropriate service provider to project location.

Submission for maintenance service via Boon Edam, Inc. Phone: 910-984-8094 or us.techsupport@boonedam.com

A geographically assigned installation provider shall be trained and certified to provide maintenance service.

COORDINATION AND SCHEDULING

Conference: Convene a pre-installation conference to establish procedures to maintain optimum working conditions and to coordinate this work with related and adjacent work per Owner request.

Coordinate sizes and locations of recesses in concrete if applicable.

Field Measurements: Verify actual dimensions for installation of the Turnlock Side Gate by field measurements before fabrication and indicate on shop drawings.

WARRANTY

Warranty: Provide manufacturer's standard warranty against defects in materials and workmanship. Warranty shall be one year from date of installation.

Warranty Period: 1 Year (12 Months)

During the warranty period a factory-trained technician shall perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair, and a completed inspection form shall be submitted to the Owner.

The Warranty excludes normal wear on finishes or damage that occurs due to abuse, misuse or acts of God.

- PRODUCTS

MANUFACTURERS

Acceptable Manufacturer: Boon Edam, Inc. 402 McKinney Parkway, Lillington NC 27546. (910) 814-3800 Fax: (910) 814-3889 Website: www.boonedam.us

Substitutions: Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.

FULL HEIGHT SECURITY SIDE ONE-WAY ELECTRIC HANDICAPPED GATE

Provide Turlock Side Gate: Electric One-way Handicapped Gate as manufactured by Boon Edam, Inc.

Provide a gate frame consisting of stainless steel or aluminum tubing welded to a flange at the base. The 24 VDC electric strike or magnetic lock to be recessed mounted into the vertical post. A one-inch hole for wiring is provided through the mounting flange.

Gate barrier to be fabricated by welding 4 sections of 2” square steel, 1.25” stainless steel or aluminum tubing. Two top and bottom horizontal components are welded to the two side sections. Round Steel tubing is welded to the horizontal members to fill in the opening is 36” with an option to extend to a 48” passage width.

A hydraulic overhead closer returns the gate swing panel to a locked position after use. Optional motorized closer available upon request for an additional cost.

Finish:

- Finishes to be available for the gate frame and door wings:

- 1.   Hot Dipped Galvanized

- .

Additional Accessory Options

Provide Credential Reader mounting plate.

- EXECUTION

PREPARATION

Installer must examine the location and advise the Contractor of any site conditions unacceptable for proper installation of product. The minimum conditions necessary to initiate installation are:

Floor must be level within 1/8” at any point within the footprint of the door.

Finished floor must be installed.

Floor must be complete with conduit supplied to meet manufacturer’s specified drawings.

INSTALLATION

- Installer must examine the location and advice the Contractor of any site conditions unacceptable for proper installation of the product.

- A level concrete floor is required to ensure proper installation. Recommended depth is at least 4 inches.

- Floor must be dead level at any point within the footprint of the gates.

- The gate is to be aligned in its proper position prior to any work beginning. A gap of 1/8” to ¼” between the lock section of the gate frame and gate barrier is suggested. Once the gate is aligned, the 2 mounting holes at each mounting flange must be marked on the concrete surface.

- The posts can be installed by using a minimum 3/8/” x 3” wedge anchor for each mounting hole. (Anchors not included)

- Electrical connections are made through the base of the latching post to the door strike or magnetic lock.

- After floor mounting the gate frame needs to be braced at the top to prevent unwanted lateral movement.

FIELD QUALITY CONTROL

Manufacturer's Field Services:

Manufacturer's representative shall provide technical assistance and guidance for installation of Turnlock Side Gate

ADJUSTING

- 1.	 Installer shall adjust gate, hardware and sensors for smooth operation and proper performance.

- 2.    Installer to confirm coordination with contractors responsible for all required connections      including access control.

DEMONSTRATION AND TRAINING

    - A factory-trained installer shall demonstrate to the Owner’s maintenance crew the proper operation of the Turnlock Side Gate and the necessary service requirements such as lubrication, cleaning, and inspection of components upon completion of installation.

CLEANING AND PROTECTION

    - Clean metal and glass surfaces carefully with non-abrasive cleaner using manufacturer’s suggested cleaning materials.

END OF SECTION