SECTION 08 42 33

SECURITY PEDESTRIAN PORTAL

- GENERAL

SECTION INCLUDES

Security Automatic Door System of the following type:

Curved side walls, canopy, ceiling, door wings, motor drive systems, and security system as required for installation (Circlelock Security Automatic Portal.)

RELATED SECTIONS

Section 07915- Sealant, Caulking and Seals

Section 08345- Security Interlocking Door Systems (Portals)

Section 08400- Entrances and Storefronts

Section 087100- Door Hardware

Section 08810- Glass and Glazing

Section 09600- Flooring

Section 16123- Electrical Supply and Termination

Section 260526- Grounding and Bonding for Electrical Systems

Section 281000- Electronic Access Control and Intrusion Detection

Section 281300- Access Control

Section 281400- Access Control System and Hardware

Section 281600- Intrusion Detection

REFERENCES

American National Standards Institute (ANSI):

ANSI Z97.1 - Safety Glazing Material Used in Buildings.

Fenestration & Glazing Industry Association (FGIA)- previously known as the American Architectural Manufacturers Association (AAMA):

AAMA 611- Voluntary Specification for Anodized Architectural Aluminum

AAMA 2604- Voluntary specification, Performance requirements and Test Procedures for High Performance Organic Coatings on Aluminum Extrusion and Panels.

AAMA 2605- Voluntary specification, performance requirements and Test Procedures for Superior Performing Organic Coatings on Aluminum Extrusions and Panels.

American Society for Testing and Materials (ASTM):

ASTM A 480/A 480M- Standard Specification for General Requirements for Flat Rolled Stainless and Heat-Resisting Steel Plate, Sheet, and Strip

ASTM B 209 – Standard Specification for Aluminum and Aluminum-Alloy Sheet and Plate

ASTM B 221- Standard Specification for Aluminum and Aluminum- Alloy Extruded Bars, Rods, Wire, Profiles, and Tubes.

Canadian Standards Association. (CSA Group)- CSA22.2#247

Underwriters Laboratories Inc. (UL)

UL Standard 325

UL Standard 2593

SUBMITTALS

Submit under provisions of Section 01 30 00 - Administrative Requirements.

Product Data: Submit manufacturer's product data sheets, including installation details, material descriptions, dimensions of individual components and profiles, fabrication, operational descriptions, and finishes:

Preparation instructions and recommendations.

Storage and handling requirements and recommendations.

Installation methods.

Shop Drawings: Submit manufacturer's shop drawings, including pertinent dimensions, general construction, component connections and locations, anchorage methods and locations, sensors, hardware, and installation details.

Operation and Maintenance Manual: Submit manufacturer's operation and maintenance manual.

Selection Samples: Submit two sets of samples showing manufacturer's standard range of available finishes.

QUALITY ASSURANCE

Manufacturer's Qualifications:

Specialization in the supply of automatic security revolving doors with a minimum of 10 years’ experience.

Factory-Trained supervisor shall be supplied during installation of the security automatic pedestrian portal.

Installer's Qualifications:

Locally located factory-trained field service technician shall be provided to competently service the automatic security revolving door; and to provide for the local support of the customer’s service technicians in the event the customer’s trained technician is not available. In the event there are no service technicians matching the aforementioned description and requirements, the manufacturer, Boon Edam, Inc., is to be utilized for service.

Local certified Boon Edam, Inc. distributor required if not being installed by the manufacturer, Boon Edam, Inc.

Approved by manufacturer.

Single Source Requirements: To the greatest extent possible provide products specified in this section from a single manufacturer.

DELIVERY, STORAGE, AND HANDLING

Delivery: Deliver materials to site protected from damage.

Storage: Store materials in clean, dry area indoors, off ground in manufacturer's unopened packaging until ready for installation and in accordance with manufacturer's instructions.

Handling: Protect materials and finish from damage during handling and installation.

PROJECT CONDITIONS

Maintain environmental conditions (temperature, humidity, and ventilation) within limits recommended by manufacturer for optimum results. Do not install products under environmental conditions outside manufacturer's absolute limits.

Circlelock installs on finished floor only.

Circlelock to be installed within a building or protected interior vestibule.

Floor must be dead level at any point within the footprint of the security automatic revolving door.

MAINTENANCE SERVICE

The manufacturer shall offer a dispatch procedure that shall be available 24 hours per day, 365 days per year to facilitate proper service capability.

A manufacturer's designated service contact shall obtain malfunction information and dispatch appropriate service provider to project location.

Submission for maintenance service via Boon Edam, Inc. Phone: 910-984-8094 or us techsupport@boonedam.com

A geographically assigned installation provider shall be trained and certified to provide maintenance service.

COORDINATION AND SCHEDULING

Conference: Convene a pre-installation conference to establish procedures to maintain optimum working conditions and to coordinate this work with related and adjacent work.

Coordinate sizes and locations of recesses in concrete if applicable.

Field Measurements: Verify actual dimensions of openings to receive revolving door entrances by field measurements before fabrication and indicate on shop drawings.

WARRANTY

Warranty: Provide manufacturer's standard warranty against defects in materials and workmanship. Warranty shall be one year from date of installation.

Warranty Period from date of ship date: 1 Year (12 Months)

During the warranty period a factory-trained technician shall perform service and affect repairs. A safety inspection shall be performed after each adjustment or repair, and a completed inspection form shall be submitted to the Owner.

The Warranty excludes glass breakage, normal wear on finishes or damage that occurs due to abuse, misuse or acts of God.

- PRODUCTS

MANUFACTURERS

Acceptable Manufacturer: Boon Edam, Inc. 402 McKinney Parkway, Lillington NC 27546. (910) 814-3800 Fax: (910) 814-3889 Website: www.boonedam.us

Substitutions: Not permitted.

Requests for substitutions will be considered in accordance with provisions of Section 01 60 00 - Product Requirements.

SECURITY AUTOMATIC REVOLVING DOOR

Security Automatic Revolving Door: Circlelock designed Single Direction Stereovision (SD) CL200SV-SD and Dual Direction Stereovision (DD) CL200SV-DD as manufactured by Boon Edam, Inc.

Provide side walls and canopy constructed from six (6) extruded aluminum posts, two (2) 2” x 2” (50 mm x 50 mm) aluminum posts, four (4) 12” (300 mm) high one-piece extruded canopies and four (4) extruded aluminum bottom rails. Overall, Height 8’6” tall.

Overall, Height 8’6“tall.

Provide two non-collapsing sliding door panels manufactured of 1 ¾” wide aluminum extrusions.

Ceiling to be fabricated of formed aluminum sheet. Ceiling must be secured using keyed locks on access panel, keys not to be removable in the unlocked position. Provide tamper switch installed in access panel to be monitored by access control. Access panel to contain safety catches and be removed only be authorized personnel.

Surface mount track to be installed on dead level finish floor.

Performance/ Throughput Requirements:

General: The security portal must be a 2-panel TWO-WAY TRAFFIC door. Throughput is defined as the number of people per minute which can pass through a door in one direction only.

Throughput is a function of the time required for complete passage divided into a one-minute time frame. Given that complete passage takes 10-15 seconds the maximum throughput is any one direction is 5-6 people per minute. Taking into consideration two factor authentication the average expected throughput in any one direction may be reducded to 3 to 4 people per minute.

Active/Passive Piggyback detection.  For throughput enhancement, the door shall be capable of selective control which allows switching between actively blocking and rejecting attempted piggyback attempts, or passive detection with allowed passage and alarm notification to Security of a potential piggyback attempt.   Selective control is managed through the Access Control System.

Finish:

- Finishes to be available for the enclosure walls, rotating door panels, and ceiling.

Powder Coatings to be AAMA 2604 High performance Organic Coatings.

Components:

- 1.  All curved glass to be ¼” clear bent tempered safety glass. All glass to meet ANSI Standard Z97.1

- 4. All commercial grade extrusions to be of aluminum alloy 6063- T6 per ASTM B-221.

- 5. Aluminum sheets to meet ASTM B-209 and be of .063 minimum thickness.

- 5. Genuine mohair weather stripping to be installed all required edges of doors wings to provide a seal between each of the door wings and drum that meets ASTM-E-283.

SEQUENCE OF OPERATION

Sequence of Operation: The sequence of operation is critical to the management of false rejections and mitigating risks of false acceptances. The specification requires the exact sequence of operation to be incorporated into the design.

In-Bound Sequence Including Stereovision and Two Factor Authentication (Optional) functionality: Authorization device located at Circlelock entrance (not provided by Boon Edam, Inc.)

Credential authorization required to activate authorization sequence of Circlelock.

Upon authorization signal, door visual indicators will change from RED to GREEN coinciding with an audible alert. Alert is designed to indicate authorization is approved.

Person (s) steps into the compartment Infrared Start-Up sensors (IRS) detect the person’s presence.

If a person does not step into the presence of the IRS, the door will time out and resent to Standby mode (i.e., Green Indicator will change to Red)

When the user enters the compartment, the Stereovision system will perform an analysis to determine if zero persons, one person, more persons or suspicious activity is present in the compartment.

Zero Persons: No presence detected by Stereovision.

One Person: Stereovision has determined there is one person in the compartment.

More Persons: Stereovision has determined there are more persons present in the compartment.

Suspicious Activity: Stereovision is unable to confirm one or more persons.

If More or Suspicious persons are in the compartment, the Stereovision system will signal to the PLC of the condition and the door will reopen. An audible alarm will sound, and visual RED indicator will flash. The door will remain open to allow the unauthorized person(s) to exit. Once the person(s) have exited, the door will resume standby mode.

If Zero persons are in the compartment the Stereovision system will send a signal to the PLC (Programmable Logic Computer) of condition and the door will begin it’s closing cycle.

As the door is reaching fully closed, the Stereovision system will perform a second analysis to verify whether Zero persons, One person, More persons or suspicious activity is present within the compartment.

If More or Suspicious persons are in the comapartment Stereovision will send a signal to the PLC of the condition and the door will reopen to allow the person(s) to exit. Once the person(s) have exited, the door will resume standby mode.

If Zero persons are in the compartment the Stereovision system will send a signal to the PLC of the condition to resume standby mode.

If One persons are in the compartment the Stereovision system will send a signal to the PLC of the condition, the door will await the following:

Biometric Approval: secure side door panel will open allowing the User to exit into the secure space.

Biometric Rejected: Non secure side door panel will open allowing the User to exit into the non-secure space.

Time Exceeded: Non-secure side door panel will open allowing the User to exit into the non-secure space.

- (When Two-Factor Authentication is disabled the secure side door will open following the completion of the Stereovision analysis)

Either door will remain open until presence is no longer detected in the compartment. Once presence is no longer detected, door panel will close, and Circlelock will resume standby mode.

Out-Bound Sequence of Operation Including Stereovision (Optional): Authorization device located at door entrance (Not provided by Boon Edam, Inc.)

Credential authorization required to activate authorization sequence of the Circlelock.

Upon authorization signal, door visual indicators will change from RED to Green along with an audible alert to indicate authorization is approved.

Secure door panel slides to the open position.

If a person does not step into the presence of the IRS, the door will time out and reset to standby mode (i.e., green indicator will change back to red)

When the User enters the compartment, the Stereovision system will perform the following analysis to determine whether zero persons, one person, more persons or suspicious activity is detected in the compartment.

Zero Persons: When no presence detected by Stereovision door system.

One Person: Stereovision has determined that there is one person in the compartment.

More Persons: Stereovision has determined that there are more persons present in the compartment.

Suspicious Activity: Stereovision is unable to confirm if there are one or more persons in the compartment.

If More or Suspicious persons are in the compartment, the Sterevision system will send a signal to the PLC of the condition and the door will reopen to allow the unauthorized person(s) to exit Once the person(s) have exited the door will close and resume standby mode.

If Zero persons are in the compartment the Stereovision system will send a signal to the PLC of the condition and the door will resume Stanby mode.

If One person(s) are in the compartment the Stereovision system will send a signal to the PLC of the condition, the door will await one of the following:

Biometric Approval: Non-Secure side of door panel will open allowing the User to exit into the non-secure space.

Biometric Rejected: Secure side of door panel will open allowing the User to exit into the secure space.

Time Exceeded: Secure side of door panel will open allowing the User to exit into the secure space.

- (When Two Factor Authentication is disabled the non-secure side door will open following the completion of the Stereovision analysis)

Either door will remain open until presence is no longer detected in the compartment. Once presence is no longer detected door panel will close, Circlelock will resume standby mode.

- EXECUTION

PREPARATION

Installer must examine the location and advise the Contractor of any site conditions unacceptable for proper installation of product. The minimum conditions necessary to initiate installation are:

Floor must be dead level at any point within the footprint of the door.

Finished floor must be installed.

Exterior grade for adequate drainage must be properly designed.

Power supply (110-240VAC) must be installed.

INSTALLATION

    - Install Circlelock in accordance with manufacturer’s printed instructions. Set unis level, plumb, and with uniform hairline joints. Anchor securely in place. Use only factory trained installers.

FIELD QUALITY CONTROL

Manufacturer's Field Services:

Manufacturer's representative shall provide technical assistance and guidance for installation of the Circlelock.

ADJUSTING

    - Installer shall adjust door, hardware and sensors for smooth operation and proper performance.

DEMONSTRATION AND TRAINING

    - A factory-trained installer shall demonstrate to the Owner’s maintenance crew the proper operation of the Circlelock and the necessary service requirements such as lubrication, cleaning, and inspection of components upon completion of installation.

CLEANING AND PROTECTION

    - Clean metal and glass surfaces carefully with non-abrasive cleaner after installation to remove excess caulk, dirt, and labels.

END OF SECTION